## Slide 1
VFCPL MARINE ENERGY PLATFORM (VFCPL-MEP-001)
Project SAMUDRA — AMBESS (Anchor Mode BESS)
American Standards (ABS ESS-LiBATTERY) & IRS Compliance
Applicant & Integrator: VFCPL (Vayusakti Future Construct Pvt. Ltd.) Battery & BMS OEM Partner: Clean Electric (307.12 Ah LFP Prismatic Cells) Domestic Rules: IRS CN Rev.1 (March 2026) & Guidelines on Battery Powered Vessels (GL Rev.2) American Rules: ABS Requirements for Lithium-ion Batteries (Dec 2025) & Notation ESS-LiBATTERY (Jan 2026) Core Architecture: Direct-Contact Dielectric Immersion-Cooled Pack with Closed-Loop Recirculation

## Slide 2
SLIDE 2 | REGULATORY HIERARCHY
Applicability Thresholds, Small Battery Rules & Class Notations
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Regulatory Domain | American Standard (ABS Dec 2025 Guide) | Indian Standard (IRS Mar 2026) | VFCPL Implementation & Verdict
Mandatory Capacity Threshold | >= 20 kWh (Lowered from 25 kWh in Apr 2024; confirmed Dec 2025). Mandatory application of ABS Part 4, Ch 8 & Guide. | Mandatory for all lithium-ion systems intended for propulsion or essential services; no lower cutoff. | COMPLIANT: MEP-001 is a full industrial commercial storage platform (> 20 kWh).
Small Battery Clause | 2 to <20 kWh (Section 1/3.1): Specific simplified rules for units in control stations. Not a blanket waiver. | Handled on plan approval case-by-case; basic IEC 62619 safety compliance required. | NOTED: MEP-001 targets the comprehensive >= 20 kWh regime; Sec 1/3.1 is not an exemption.
Class Notation Assignment | ESS-LiBATTERY (ABS Jan 2026 p.59). Optional vessel notation verifying compliant installed battery system. | BATTERY PROP (Main Propulsion) or BATTERY (PROPULSION SUPPORT) (Auxiliary/Hybrid). | ALIGNED: AMBESS qualifies for ESS-LiBATTERY and BATTERY (PROPULSION SUPPORT).
US Statutory Framework | USCG NVIC 02-19, 46 CFR Subchapter J (Electrical), NFPA 855 (Stationary Energy). | DG Shipping Merchant Shipping Rules & IMO MSC.1/Circ.1453 & Circ.1647. | ACTION REQUIRED: Submit thermal propagation & FMEA reports to USCG MSC for US flag.
CRITICAL RULE INTERPRETATION (Section 1/3.1 of Marine BESS.docx): Section 1/3.1 addresses 2 to <20 kWh systems located in control stations; it is NOT a blanket waiver for smaller batteries. Because VFCPL-MEP-001 is an industrial marine energy storage system with scalable capacity exceeding 20 kWh, the full ABS guide applies unconditionally.

## Slide 3
SLIDE 3 | CERTIFICATION PATHWAYS
What Certificate Should a BESS Supplier Seek? (Section 3)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
1. Product Design Assessment (PDA)
ABS Design Assessment (5-Yr Validity)
• Technical review of defined product against stated rules & standards.
• Review of engineering drawings, SLDs, thermal models, and FMEA.
• Verification of accredited cell test reports (IEC 62619, IEC 62620).
• Verification of thermal runaway propagation evidence (UL 9540A).
• Satisfies technical design review for any shipyard or project.
2. Manufacturing Assessment (MA)
ABS Factory & Works Assessment
• Assessment of factory production and quality control processes.
• Applies to Clean Electric (BMS/modules) and VFCPL (pack assembly).
• Requires ISO 9001:2015 certified quality management system.
• Requires annual surveillance plant audits by attending surveyor.
• Guarantees manufactured units reproduce the assessed design.
3. Type Approval & Unit Cert
ABS Type Approval = PDA + MA Combined
• ABS Type Approval: Granted when PDA + MA are completed together.
• Allows off-the-shelf procurement for shipyards without repeat reviews.
• Unit Certification: Testing the physical delivered ship units at the manufacturer with an ABS surveyor.
• Generic product assessment does not settle every installation condition.
PURCHASING & OEM SOURCING DISTINCTION (Section 3 of Marine BESS.docx): A logo or certificate front page cannot establish whether your complete offered configuration is covered. Request the certificate, schedule, model list, and site details. Because VFCPL imports cells and builds modules/racks in India, the application must identify OEM design ownership (Clean Electric) vs. secondary pack manufacturing (VFCPL).

## Slide 4
SLIDE 4 | BASELINE STANDARDS
What Each Standard Proves: IEC 62619, IEC 62620, UN 38.3 & UL (Section 5)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Standard / Evidence | Primary Scope & Purpose | How to Use in VFCPL Project | Class Evidence Status
IEC 62619:2022 | Industrial lithium cell/battery safety (drop, impact, short circuit, thermal abuse). Required by ABS Sec 2/1.2 & IRS CN Rev.1 §1.4.c. | Obtain full test reports identifying tested cell and assembly; verify certificate scope matches supplied 307 Ah product. | ACCEPTED (Clean Electric report)
IEC 62620:2014+AMD1:2023 | Industrial cell/battery marking and performance requirements (capacity verification, endurance, discharge rates). | Connect declared capacity (307.12 Ah) and test configuration to marketed model. Record the 2023 amendment explicitly. | ACCEPTED (Marking & Rating confirmed)
UN 38.3 Evidence | Transport-related battery design testing (T1-T8 altitude, thermal, vibration, shock, short circuit). | Maintain separately from marine installation approval dossier. Do NOT present as proof of complete onboard operational safety. | ACCEPTED (Transport dossier)
UL 9540A Results | Thermal runaway / fire propagation characterization (cell, module, unit, installation levels). | Use as supporting hazard evidence; obtain class agreement on equivalence to specified class test. | SUBMITTED (Thermal bench data)
CHANGE CONTROL MANDATE (ABS Section 1/7 & IRS CN Rev.1 Section 1.10): Confirm no substantial change has been made to the cell active material, internal chemistry, casing dimensions, or manufacturing site since the test certificates were issued. Any such alteration invalidates the Type Approval unless submitted and approved in advance.

## Slide 5
SLIDE 5 | THERMAL SAFETY & RUNAWAY
Thermal-Runaway Evidence: The 7 Review Questions (Section 8)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
The 7 Review Questions to Make Reports Usable
1. Cell Construction Authenticity: Does the tested cell have exactly the same construction as the purchased cell? 2. SOC & Conditioning: Does report identify SOC (100%), conditioning, initiating method, and sample orientation? 3. Worst-Case Arrangement: Was the tested assembly representative of the most challenging offered arrangement? 4. Active Systems State: Were cooling (pump P1) and protective systems running, failed, or unavailable? 5. Propagation Containment: What happened to adjacent cells/modules, enclosure pressure, and gas release? 6. Measured Gas/Heat Data: Are measured gas/heat data sufficient for the integrator's ventilation and fire analysis? 7. Invalidation Boundaries: Which changes in spacing, barriers, enclosure, firmware, or coolant invalidate the inference?
Class Propagation Rules & Immersion Physics
ABS Section 2/2.1 Mandate: The battery system must prevent cell-to-cell propagation, or at minimum demonstrate module-to-module containment with zero external flaming and casing temperature < 100°C. UL 9540 vs. UL 9540A Distinction: UL distinguishes UL 9540A test method from UL 9540 complete-system certification criteria. A report from one does NOT justify describing a product as certified to the other. VFCPL Direct Immersion Advantage: The dielectric fluid conducts heat away immediately, suppressing runaway trigger points. In bench tests, zero cell-to-cell propagation occurred across adjacent LFP cells.

## Slide 6
SLIDE 6 | IMMERSION COOLING ENGINEERING
Liquid & Immersion Cooling: Hydrotest & Failure Detection (Section 2 & 4)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Engineering Checkpoint | ABS Dec 2025 Rules (Sec 2/2.4 & 3/2) | IRS CN Rev.1 / GL Rev.2 Requirements | VFCPL-MEP-001 Baseline & Status
Shop Fabrication Hydrotest | 1.5 x Design Pressure for 30 minutes during manufacturing. Zero leakage permitted. | CN Rev.1 5.2.d.viii: Pressure test to verify pressure-withstanding capacity. | GAP CLOSED: Formally standardized in VFCPL QA SOP-004 (1.50 bar, 30-min hold).
Installation Tightness Test | Tested at 1.0 x Design Pressure following shipboard installation. Zero leak. | GL Rev.2 §3.3.3 functional test post-installation. | COMPLIANT: Pre-commissioning leak check procedure prior to fluid fill.
Pipe Routing Over Live Parts | No mechanical pipe joints directly over live electrical components unless shielded. | GL Rev.2 2.3.4: Protection against fluid ingress and leakage onto live parts. | COMPLIANT: Monolithic immersion tank; no internal pipe joints. Non-conductive oil.
Cooling Failure Alarms | Loss of coolant flow or high coolant temp must raise immediate alarm at manned station. | CN Rev.1 4.4.k & GL Rev.2 2.3.9.m: Cooling failure alarm mandatory. | COMPLIANT: Pump P1 current sensing and Delta-T thermistors (T1-T6) feed BMS.
AMBESS PUMP P1 CONTROL ARCHITECTURE (IRS Submission Rev A): Closed hydraulic circuit: pack immersion channel -> circulating pump P1 -> direct return. Pump operates on dual interlock: Condition A (Fast charging current threshold) and Condition B (Delta-T > 2.5°C across T1-T6 thermistors), equalizing cell temperatures and delivering 89.65% SOH retention over 818 cycles.

## Slide 7
SLIDE 7 | COOLANT FLUID SPECIFICATIONS
Dielectric Coolant Fluid: Electrical, Fire & Environmental Properties
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Electrical Insulation
• Dielectric Breakdown: > 50 kV (IEC 60156 / ASTM D877).
• Volume Resistivity: > 10^12 Ohm-m at 25°C.
• Prevents arcing across live busbars up to 1000 VDC even during dynamic vessel motion.
• Eliminates conductive path hazards common to water-glycol cold plates.
Thermal & Fire Safety
• Flash Point: > 160°C (ISO 2719 Closed Cup).
• Fire Point: > 190°C (ISO 2592 Open Cup).
• Auto-ignition: > 350°C.
• Kinematic Viscosity: < 35 mm²/s at 40°C; < 3000 mm²/s at -20°C (ASTM D7042).
• Cold-start pumping validated down to -20°C.
Marine Environmental & Life
• Biodegradability: Readily biodegradable (>60% in 28 days, OECD 301B).
• Aquatic Toxicity: Non-toxic to marine organisms (OECD 201, 202, 203).
• Material Compatibility: Zero chemical degradation on NBR/FKM gaskets and copper busbars over 10-year life.
• Non-hazardous for shipboard handling and storage.
LONG-TERM COMPATIBILITY MANDATE (ABS Section 2/2.5 & IRS CN Rev.1 §1.4.d): Both ABS and IRS mandate verification that the dielectric fluid exhibits zero chemical degradation, swelling, or extraction on internal gaskets (NBR/FKM), wire insulation, potting resins, and cell sealants across the 10-year service life. Test reports per ASTM D471 are compiled in Folder 5.

## Slide 8
SLIDE 8 | BMS SAFETY & FIRMWARE
BMS Safety Architecture: Critical Overrides Prohibited (Section 2 & 4)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
ABS BMS Rules (Section 2/5)
• Critical Overrides Forbidden (Sec 2/5.1): No manual override or software bypass is permitted for critical safety shutdowns (overvoltage, undervoltage, overtemperature, short circuit). • Physical vs. CAN Status Fallacy (Sec 7): A CAN status message indicating "safe" does NOT establish that a physical isolation device actually opened. Auxiliary contact feedback required. • Loss of Communication Safe State: Communication timeout (>250ms) between BMS Master and Slave CSCs reverts system to an immediate fail-safe trip.
Clean Electric BMS Implementation
• 100% Cell-Tab Voltage Coverage: Direct measurement of every series cell tab; 6 thermistors across immersion pack feed BMS. • Hardcoded Non-Volatile Lockout: Safety threshold tripping is hardcoded in firmware flash; zero operator override mode exists. • Dual Independent Isolation: Positive and negative poles fitted with fast-acting DC contactors backed by series semiconductor pyro-fuses. • Active Insulation Monitoring (IMD): Bender IMD integrated: pre-warning alarm at 100 Ohm/V; automatic trip at 50 Ohm/V.
IRS 2026 BMS AMENDMENTS (Section 4 of Marine BESS.docx): The March 2026 IRS BMS amendments identify mandatory alarms for voltage imbalance, low insulation, cooling failure, and communication failure. Applicable for certification applications dated from 1 July 2026 and equipment fitted on vessels contracted from that date.

## Slide 9
SLIDE 9 | ENVIRONMENTAL TESTING
Marine Environmental Qualification: IACS UR E10 (Section 6)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Test Description | Standard Reference | Test Parameters & Levels | Hardware Under Test & Status
Power Variations | IACS UR E10 Test 3 | DC +/-20% steady; 0V drop for 5ms; ripple 10% | BMS 24VDC control supply [GAP - Test lab]
Dry Heat & Cold | IACS UR E10 Tests 4 & 6 | +70°C for 16h operational; -25°C for 2h operational | Master BMS & Slave CSCs [GAP - Test lab]
Damp Heat | IACS UR E10 Test 5 | +55°C at 95% RH (cyclic, 2 cycles of 24 hours) | All PCBs (conformal coating check) [GAP]
Sinusoidal Vibration | IACS UR E10 Test 7 | 2-13.2 Hz (+/-1.0mm); 13.2-100 Hz (0.7g) on 3 axes | Immersion pack, pump & casing [GAP]
Inclination Test | IACS UR E10 Test 8 | Static roll/pitch 22.5°; dynamic roll 22.5° (10s period) | Verifies no pump cavitation [GAP]
EMC & Salt Mist | IACS UR E10 Tests 10 & 15-21 | Radiated/conducted, burst, surge, ESD; 28d salt mist | BMS comms lines and connectors [GAP]
OPERATING ENVELOPE CHART PRINCIPLE (Section 6 of Marine BESS.docx): Separate the cells' allowable operating range, the rack's qualified ambient range, the BMS electronics' test conditions, and cooling capacity. Build a single operating-envelope chart showing which limit constrains the complete BESS. Testing a composite system does not generate separate certificates for individual components.

## Slide 10
SLIDE 10 | ELECTRICAL PROTECTION
Electrical Protection: Fault Current, Pre-charge & Isolation (Section 7)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Isolation vs. Containment Argument
Critical Principle (from Section 7): Opening a DC contactor cannot remove energy already stored inside electrochemical cells. Independent Systems: Separate the electrical-isolation argument from the heat/gas-containment argument in your design review. Prospective Fault Current (Isc): Calculated per IEC 61660-1. Due to extremely low internal cell resistance (Ri), fault current rise (di/dt) is steep. Sub-Millisecond Clearance: Semiconductor DC pyro-fuses (>20 kA breaking capacity) in series with positive and negative poles clear dead short circuits before contactor welding occurs.
Pre-Charge & Ungrounded IT Bus Isolation
Pre-Charge Resistor Circuit: Limits DC link capacitor inrush current to <1.0C during inverter connection; contactor interlocked with inverter DC bus voltage (>95% VDC before main contactor closes). Continuous Insulation Monitoring (IMD): Floating ungrounded IT DC distribution network with active Bender ground-fault detector measuring insulation resistance across both poles. Pre-Warning Alarm Threshold: 100 Ohm / Volt. Critical Trip Threshold: 50 Ohm / Volt with automatic system isolation. Selective Protection: Coordinated selectivity ensures string fuses clear branch faults without tripping the vessel main switchboard.

## Slide 11
SLIDE 11 | ENCLOSURE & INGRESS
Mechanical Enclosure, Ingress Protection & Pressure Relief
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Ingress Protection (IP Code)
• ABS Section 2/2.2 requires minimum IP44 in dedicated battery spaces and IP67 on open weather decks.
• IRS INST-04 recommends minimum IP44.
• VFCPL Monolithic Enclosure is certified to IP67 throughout (dust-tight and protected against water immersion).
• Exceeds standard battery room requirements and permits exposed containerized mounting.
Thermal Volumetric Breathing
• Dielectric fluid expands with temperature changes (volumetric expansion coefficient beta ~ 0.0007 /°C).
• Internal headspace cushion or expansion bellows accommodates fluid expansion across -10°C to +65°C.
• Prevents internal overpressure during normal cycling without casing deformation.
• Sealed breather with desiccant prevents atmospheric moisture ingress.
Pressure Relief Valve (PRV)
• Spring-loaded PRV or rupture disc calibrated below elastic deformation limit of aluminum shell.
• Sized to discharge peak off-gas generation volume during worst-case thermal runaway.
• Discharge port flanged for direct connection to shipyard exhaust duct.
• Piped directly to open weather deck away from personnel and air intakes.

## Slide 12
SLIDE 12 | COMPARTMENT & VENTILATION
Battery Space Design, Ventilation & Hazardous Area Zoning
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Engineering Parameter | ABS Dec 2025 Rules (Sec 3/3 & 3/5) | IRS GL Rev.2 Requirements (Sec 2.2 & 2.6) | VFCPL Integration Specification
Room Boundary Fire Rating | Machinery Space of Category A. Structural fire protection A-60 towards high risk areas. | Category A space treatment. A-60 boundaries adjacent to accommodation and control spaces. | Shipyard integration drawings specify A-60 bulkheads and self-closing fire doors.
Normal Ventilation | Mechanical ventilation maintaining compartment <= 35°C. Independent ducting. | Independent mechanical ventilation providing minimum 2 Air Changes per Hour (ACH). | Dedicated supply & exhaust HVAC with intake near floor and exhaust at ceiling level.
Emergency Ventilation | Mandatory high-rate exhaust triggered automatically upon flammable gas detection. | Minimum 6 Air Changes per Hour (ACH) starting automatically on gas detection. | Dual-speed spark-proof blower interlocked with BMS / Gas Detection panel.
Hazardous Area Zoning | Classified per IEC 60079-10-1. Zone 2 where battery off-gas can accumulate. | Zone 2 classification. Certified safe electrical equipment at least Ex IIC T1. | All room lighting, gas sensors, fan motors, and actuators certified ATEX/IECEx Zone 2 Ex-d/ia.
SPARK-PROOF FAN CONSTRUCTION (GL Rev.2 §2.6.1.3 & ABS Sec 3/3.3): Exhaust fans must feature anti-static, non-metallic spark-minimizing impellers with Ex-d explosion-proof motors. The emergency exhaust fan must start automatically on gas detection and be operable remotely from the bridge and locally outside the battery space.

## Slide 13
SLIDE 13 | FIRE & GAS SAFETY
Fire Detection, Gas Monitoring & Water-Based Extinguishing
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Gas & Fire Detection Architecture
Smoke Detection: Addressable optical smoke detectors complying with IMO FSS Code positioned throughout the compartment. Off-Gas Flammable Gas Detectors (LEL): • At 30% LFL: Audio-visual alarm at manned control station, automatic start of 6 ACH emergency ventilation, and controlled BMS trip. • At 60% LFL: Total automatic de-energization of all non-Ex electrical circuits in the compartment. Thermal Imaging: Fixed thermographic / IR cameras recommended by IRS GL Rev.2 §2.6.4.2 to monitor external surface temperatures.
Fixed Water-Based Fire Extinguishing
Mandatory Water-Based Extinguishing: Fixed water mist or sprinkler system approved for Category A machinery spaces (IMO MSC.1/Circ.1165). Why Gaseous Systems are Rejected: Class rules reject purely gaseous systems (CO2, Novec 1230, FM-200) as primary lithium runaway protection because gases starve oxygen but cannot extract deep internal heat from burning cells. Immersion Protection Synergy: In the VFCPL pack, internal cell cooling is provided by the dielectric fluid. External water mist protects the room structure, cools the exterior casing, and suppresses external fires.

## Slide 14
SLIDE 14 | CONTAINERIZED SYSTEMS
Packaged & Containerized Marine BESS (ABS Appendix 3 & Section 9)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Structural & Marine Lifting
• ISO container structure certified to International Convention for Safe Containers (CSC).
• Offshore lifting lugs certified to DNV 2.7-1 / ISO 10855 for marine crane operations.
• Deck tie-down structural calculations verifying survival under severe vessel heave, pitch, and roll accelerations.
• Finite Element Analysis (FEA) verifying deck weld withstand.
Fire Separation & Boundaries
• Container outer envelope insulated to A-60 fire standard throughout.
• Located away from life-saving appliances (lifeboats, liferafts) and muster stations.
• Clear of accommodation air intakes and hazardous fuel tanks.
• Self-closing doors with limit switches feeding wheelhouse alarms.
Integrated Safety Systems
• Internal Fire & Gas (F&G) detection and deluge control head inside container vestibule.
• External Emergency Shutdown (ESD) button outside container access door.
• Self-contained HVAC system with automatic fast-closing fire dampers.
• Dedicated exhaust louvers interlocked with deluge release.
CONTAINER SCOPE ALLOCATION WARNING (from Section 9 of Marine BESS.docx): For containerized supply, explicitly identify whether HVAC, fire detection, suppression, exhaust, converter, and auxiliary power are included. A container shell certificate alone says little about the electrical and thermal safety of the contents.

## Slide 15
SLIDE 15 | AMBESS OPERATIONAL CONCEPT
AMBESS Operational Concept: Hotel Power & Essential Services
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Anchor Mode Operating Philosophy
Duty Profile: Supplies vessel hotel and auxiliary electrical loads during anchor watch or station keeping, allowing diesel generators to be shut down. Generator Optimization: Generators operate in short, high-efficiency blocks (>75% MCR) to recharge BESS, avoiding low-load (<30%) engine wet-stacking. Solar Offset: Integrated DC/DC solar array offsets auxiliary charging demand in port/anchorage. Demonstrated Cycle Life: Bench validated over 818 cycles with 89.65% capacity retention (SoH) and minimal cell degradation.
Essential Services & Redundancy Rules
Auxiliary Role vs. Main Propulsion: AMBESS is classed as Auxiliary Power / Propulsion Support under IRS GL Rev.2 §1.1.3 and ABS Section 4. Blackout Prevention Interlocks: A fault, trip, or short-circuit on the BESS DC bus must NEVER backfeed or cause tripping of primary shipboard diesel generators or steering gear. Propulsion Redundancy Exemption: Because AMBESS is dedicated to hotel/auxiliary power and does not power the vessel propulsion shaft line, mandatory dual redundant battery rooms and split propulsion switchboards are NOT required. Saves significant capital cost and structural space for shipowners.

## Slide 16
SLIDE 16 | 10 ENGINEERING WORK PACKAGES
The 10 Engineering Work Packages for the BESS Supplier (Section 7)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Work Package | Evidence VFCPL & Clean Electric Must Assemble | Decision to Close
1. Product Definition | Architecture, model codes, cell OEM, series/parallel configuration, DC voltage window, energy/power ratings. | Exactly which variants belong to the approval family?
2. Cell Sourcing | Full test reports (IEC 62619/62620), lot traceability, storage history, supplier change notices. | Which supplier/model substitutions trigger reassessment?
3. Module Mechanics | Drawings, connection design, weights, centre of gravity, fastening and service access. | Which installation loads and mounting arrangements are approved?
4. Electrical Protection | Prospective fault-current calculation (Isc), fuse/breaker selection, contactor ratings, precharge and isolation. | Can each credited device interrupt or withstand the actual fault?
5. BMS Architecture | Architecture, signal list, fault handling, software release controls and diagnostic coverage, override lock. | What is the safe response to each sensor, processor or comms fault?
6. Cooling Engineering | Heat map, thermal model, fluid specification, flow/pressure limits, leakage controls and hydrotest evidence. | Which faults require derating, isolation or shutdown?
7. Off-Gas & Fire | Chemistry-specific test results, release paths, pressure relief and interfaces to protective systems. | Which protective functions are inside the product boundary?
8. Converter Interface | Limits, commands, feedback, timeout rules, stop sequence and restart conditions. | Does each end behave consistently when the other end fails?
9. Production Assurance | Incoming inspection, assembly records, torque control, end-of-line records and calibration. | How is every delivered unit connected to the assessed design?
10. Field Support | Installation limits, servicing instructions, spares policy, software updates and event retrieval. | How are unauthorized changes and configuration drift prevented?

## Slide 17
SLIDE 17 | SUPPLIER-SHIPYARD BOUNDARY
Supplier vs. Shipyard Responsibility Boundary Schedule (Section 9)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Interface Domain | BESS Supplier Provides (VFCPL & Clean Electric) | Integrator / Shipyard Closes
1. DC Electrical Power | Voltage/current envelope, terminal details, fault contribution calculation (Isc), fuses, contactors. | Distribution switchboard, cabling, upstream coordination, A-60 cable transits, blackout interlocks.
2. Immersion Cooling | Sealed tank, internal dielectric fluid, pump P1, failure alarms, 1.5x hydrotest QA certificate. | Space ventilation (<=35°C), post-installation 1.0x tightness test, wheelhouse AMS alarm wiring.
3. Off-Gas & PRV | Calibrated PRV, outlet geometry, gas volume rate, allowable backpressure data. | Dedicated steel exhaust duct directly to weather deck (>=3m from air intakes), flame arrestor.
4. Emergency Shutdown | Hardwired discrete ESD input terminals (24VDC fail-safe), dual contactors, feedback telemetry. | Remote ESD buttons at bridge, CCR, and outside room door; end-to-end trip verification.
5. Fire Protection | Immersion fluid containment data, material safety data, post-fire hazard guidelines in manual. | A-60 structural boundary, IMO FSS smoke detectors, fixed water-based fire extinguishing (water mist).
6. Hazardous Area | Gas emission data, IP67 enclosure rating, BMS trip signal on gas input. | Zone 2 classification, electrical equipment certified Ex IIC T1, gas detection trips at 30% & 60% LFL.
7. Mechanical & Structural | Wet mass, 3D Center of Gravity, dynamic acceleration load factors, mounting layout, lifting lugs. | Deck foundations, structural coaming, deck load calculation, 600 mm maintenance access clearance.
8. Communications | Isolated CAN/Modbus port, register map, dynamic current limits (CCL/DCL), heartbeat watchdog. | Ship EMS/PMS driver, generator ramp-rate coordination, wheelhouse alarm & monitoring panel.

## Slide 18
SLIDE 18 | SUBMISSION DOSSIER STRUCTURE
Controlled Submission Folders & 4-Tier Evidence States (Section 11)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
The 8 Controlled Submission Folders
• Folder 1: Basis Intended use (AMBESS hotel power), exclusions, rule editions, model family, approval strategy. • Folder 2: Design Electrical SLD, mechanical drawings, BOM, fluid schematics, PRV sizing calculations. • Folder 3: Safety Hazard register, FMEA, protective trip matrix, unresolved installation assumptions. • Folder 4: Controls BMS specs, override lockout statement, CAN map, Software Quality Plan (SQP). • Folders 5-8: Thermal, Testing, Manufacturing, Delivery Fluid test data, accredited lab test reports, ISO 9001 QA SOP-004, and shipyard manuals.
The 4-Tier Evidence States (Section 11)
Avoid a single "compliant" column: A design intention, a test result, and class acceptance are fundamentally different levels of evidence. 1. ACCEPTED: Formally approved in writing by the classification society surveyor or plan review office. 2. SUBMITTED: Formally delivered to class; currently pending technical review. 3. GAP: Rule requirement identified, but technical evidence or test report does not yet exist; action required. 4. NOT APPLICABLE (N/A): Excluded with formal engineering justification approved by class.

## Slide 19
SLIDE 19 | DUAL-CLASS COMPLIANCE MATRIX
Complete Dual-Class Compliance Matrix & Engineering Gap Analysis
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
Subsystem | ABS Dec 2025 Guide | IRS Mar 2026 Rules | VFCPL-MEP-001 Baseline | Status & Action
System Threshold | Mandatory >=20 kWh | All propulsion/essential BESS | Modular commercial system >20 kWh | ACCEPTED
Cell Safety | IEC 62619:2022 | IEC 62619:2022 (CN Rev.1) | LFP Prismatic Cells (307 Ah) | ACCEPTED
Cell Performance | IEC 62620:2023 | IEC 62620 (CN Rev.1 §5.3) | IEC 62620 rated and laser marked | ACCEPTED
Thermal Runaway | Non-propagation test | CN Rev.1 App.1(b)#5 test | Dielectric immersion cooling bath | SUBMITTED
Shop Hydrotest | 1.5x design press, 30 min | 5.2.d.viii pressure test | Sealed aluminum casing | GAP: Formalize SOP-004
BMS Override Lock | Overrides forbidden | 4.4.h override lockout | Firmware hardcoded lockout | ACCEPTED
Environmental | IACS UR E10 (Pt 4, Ch 9) | IACS UR E10 (CN Rev.1) | Clean Electric BMS hardware | GAP: UR E10 lab test
Enclosure IP | Min IP44 space / IP67 deck | Min IP44 (GL Rev.2 2.2.8) | IP67 sealed aluminum enclosure | ACCEPTED
Ventilation | Normal + Emergency exhaust | 2 ACH normal / 6 ACH emerg | HVAC layout specification | SUBMITTED
Type Approval | ABS PDA + MA (5 Years) | IRS TA Certificate | Target certification submissions | GAP: Submit PDA package

## Slide 20
SLIDE 20 | APPROVAL ROADMAP & DECISIONS
Approval Sequence & 10 First-Meeting Decisions (Section 10 & 12)
VFCPL-MEP-001 (Project SAMUDRA) AMBESS | ABS ESS-LiBATTERY & IRS Alignment
CONFIDENTIAL - FOR CLASS & ENGINEERING REVIEW
The 8-Step Approval Sequence
1. Freeze Certification Basis: Rule editions, duty, model family. 2. Report-by-Report Gap Review: Match claims to documents. 3. Agree Test Plan Before Booking Labs: Lock lab protocols. 4. Resolve Architecture Risks: Cooling, isolation, override locks. 5. Qualify Representative Design: BOM, HW, FW control. 6. Complete Works Assessment: Factory QA audit. 7. Deliver Serial Dossier: Unit test records and deviations. 8. Support Installation: Shipyard sea trials & commissioning.
10 Decisions for First Technical Meeting
1. Confirm BESS service (auxiliary-only duty rule basis). 2. Package vs. component certificate scope. 3. Representative model and product family limits. 4. Written decision on existing IEC / ABS witnessed reports. 5. Propagation-test setup and acceptance criteria. 6. Environmental qualification locations (IACS UR E10). 7. BMS software assessment and failure simulation tests. 8. Unit-certification scope and factory hold points. 9. Installation dependencies appearing as certificate limits. 10. Change-notification thresholds for cells and firmware.